## Slide 1: SLC Parks HVAC Replacement Jarrett Capstick, P.E.

## Slide 2: Old Slc Parks building
~40,000 SF BUILDING
    12,000 SF OFFICE (FURNACE / CONDENSING UNIT)
    28,000 SF WAREHOUSE (UNIT HEATERS)
HVAC SYSTEMS PAST EXPECTED USEFUL LIFE
ZONING AND OCCUPANT COMFORT ISSUES ASSOCIATED WITH MULTIPLE REMODELS.
DESIGN STARTED SPRING 2018.
PROJECT BID (#1) SPRING 2019.
COMPLETED SPRING 2022.

## Slide 3: HVAC System Evaluation
INITIAL SYSTEM EVALUATION:
GROUND SOURCE w/ ZONE LEVEL WATER-AIR HEAT PUMPS
BOILER / COOLING TOWER w/ ZONE LEVEL WATER-AIR HEAT PUMPS
BOILER / CHILLER w/ ZONE LEVEL 4-PIPE FAN COILS
BEST VALUE WAS DETERMINED TO BE OPTION 1 WITH A 1-PIPE CONDENSER WATER LOOP DISTRIBUTION SYSTEM.
*EACH OPTION INCLUDED A DEDICATED OUTDOOR AIR SYSTEM (DOAS) FOR VENTILATION AIR

## Slide 4: HEAT PUMP SYSTEMS
WATER-TO- AIR HEAT PUMPS:
VERTICAL OR HORIZONTAL CONFIGURATION
INTERNAL COMPRESSOR, COIL, FAN, FILTER
DUCTED TO ZONE
CONDENSER WATER SUPPLY AND RETURN PIPING
OPERATION:
HEATING MODE (EWT > LWT)
ABSORB HEAT FROM CONDENSER WATER + HEAT OF COMPRESSION (~25%)
COOLING MODE (EWT < LWT)
REJECT HEAT TO CONDENSER WATER + HEAT OF COMPRESSION
CONDENSER WATER:
IDEAL TEMPERATURE IS 55°F - 85°F (EXTENDED RANGE EQUIPMENT IS AVAILABLE)

## Slide 5: HEAT PUMP SYSTEMS
PIPING STRATEGIES
2-PIPE:
1-PIPE:
EACH UNIT GETS THE SAME TEMPERATURE CONDENSER WATER.
CONTROL VALVE PER UNIT
SYSTEM PUMP(S) MAINTAIN DIFFERENTIAL PRESSURE.
EACH UNIT GETS VARYING TEMPERATURE CONDENSER WATER.
PUMP PER UNIT
SYSTEM PUMP(S) MAINTAIN LOOP TEMPERATURE.

## Slide 6: …BACK TO THE PARKS PROJECT
THE RESULT…
BUDGET
THE SOLUTION…
CHANGE FROM CONVENTIONAL TO BULLDOG HEAT PUMPS w/ 2-PIPE DISTRIBUTION
ELIMINATE GROUND SOURCE BOREFIELD
  HEAT CONDENSER WATER WITH BOILER
  REJECT HEAT WITH DRY-COOLER

## Slide 7
HEAT PUMP COOLING / HYDRONIC HEATING
COMPRESSOR OPTIMIZED FOR ELEVATED CONDENSER WATER TEMPERATURE
HEATING WATER COIL OPTIMIZED FOR LOW HEATING WATER TEMPERATURE
(HIGH CONDENSER WATER TEMPERATURE)

## Slide 8
2-PIPE:

## Slide 9
POTENTIAL ADVANTAGES
LESS COMPRESSOR RUN TIME = LONGER EQUIPMENT LIFE
QUIETER OPERATION IN HEATING MODE (NO COMPRESSOR)
GAS HEATING = LOWER OPERATING COST
LOW “HEATING WATER TEMPERATURE” = HIGHER BOILER EFFICIENCY
MODULATING HEATING CAPACITY
  *HELPFUL WHEN EQUIPMENT IS SIZED FOR COOLING CAPACITY

## Slide 10: BOILER / DRY COOLER

## Slide 11: DESIGN PIPING SCHEMATIC

## Slide 12: Heating Operation
LOOP MODULATED FROM 100°F – 110°F
BOILER MODULATED UP TO 40% FIRING RATE

## Slide 13: Cooling operation
OUTSIDE AIR TEMPERATURE REACHED 108°F
LOOP TEMPERATURE MODULATED BETWEEN 115 °F -90°F
TERMINAL UNITS WERE ABLE TO PROVIDE COOLING

## Slide 14: QUESTIONS? THANK YOU
Jarrett Capstick
801-505-5390
jcapstick@cea-ut.com